## Slide 1
Solids to disposal
Raw water from surface water source
Treated water to distribution system
Clearwell storage
Liquid processing
Residuals processing and management
Granular filtration
Flocculation
Sedimentation
pH control
Oxidant/ disinfectant
Disinfectant
Screen
Water return from waste washwater recovery system and solids dewatering
Waste washwater to water recovery system or disposal
Filter-to-waste water to recycle to head of plant
Solids to dewatering
Polymer
Filter backwash water
Flash mix
Coagulant
Figure 4-4
Typical process train for treatment of surface water by conventional treatment.
Solids to disposal
Raw water from surface water source
Treated water to distribution system
Liquid processing
Residuals processing and management
Granular filtration
Flocculation
pH control
Oxidant/ disinfectant
Clearwell Disinfectant storage
Screen
Water return from waste washwater recovery system and solids dewatering
Waste washwater Filter-to-waste to water recovery water to recycle system or disposal to head of plant
Polymer
Filter backwash water
In-line filtration
Flash mix
Coagulant
Figure 4-5
Typical process train for treatment of surface water by direct and in-line ﬁltration.
206

## Slide 2
Solids to disposal
Raw water from surface water source
Treated water to distribution system
Clearwell storage
Liquid processing
Residuals processing and management
Disinfectant
pH control
Screen
Water return from washwater recovery system
Waste washwater to water recovery system or disposal
Filter backwash water from clearwell or aternate source
Membrane filtration
Cartridge filters or microscreens
Figure 4-6
Typical process train for treatment of surface water by membrane ﬁltration.
Solids to disposal
Raw water from saline water source
Treated water to distribution system
Clearwell storage
Liquid processing
Residuals processing and management
Disinfectant
pH control
Screen
Water return from washwater recovery system
Waste washwater
system or disposal
Filter backwash
or aternate source
Reverse osmosis
Concentrate
to water recovery water from clearwell (waste stream)
to disposal
Membrane filtration
Cartridge filters or microscreens
Figure 4-7
Typical process train for treatment of saline water by reverse osmosis.
208

## Slide 3
Raw water from ground- water source
Treated water to distribution system
Clearwell storage
Liquid processing
Residuals processing and management
Granular filtration
Disinfectant
Waste washwater to water recovery system or disposal
Filter-to-waste water to recycle to head of plant
Solids to dewatering
Polymer
Filter backwash water
Recycle
Solids to dewatering
Flocculation/clarification
Lime and/or soda ash
CO2
Recarb- onation
Water return from waste washwater recovery system, solids dewatering, and filter-to-waste
Figure 4-8
Typical process train for removal of hardness (calcium and magnesium) from groundwater with lime – soda softening process.
Raw water from ground- water source
Treated water to distribution system
Liquid processing
Residuals processing and management
Clearwell
Disinfectant storage
Nanofiltration modules
Concentrate (waste stream) to disposal
Oxidant/ disinfectant
pH control
Anti- scalant
Cartridge filters or microscreens
Water return from waste washwater recovery system, solids dewatering, and filter-to-waste
Figure 4-9
Typical process train for treatment of groundwater with nanoﬁltration softening process.
209

## Slide 4
210
4 Water Quality Management Strategies
Air stripping
Air stripping is used to treat groundwater containing undesirable gases such as hydrogen sulﬁde or VOCs at levels above the MCL. An air-stripping process treatment train consists of a stripping tower followed by pressurized granular media ﬁltration and disinfection, as shown on Fig. 4-10. In some cases the use of conditioning chemicals and/or acid addition may be nec- essary to prevent the formation of precipitates. A consideration when using air stripping is treating the off-gas from the stripping tower. One method for treatment of the off-gas is carbon adsorption, as shown on Fig. 4-10.
Iron and manganese treatment
Oxidation and precipitation on pressure ﬁlters is the process used most commonly for the removal of inorganic iron and manganese typically found in groundwaters with low dissolved oxygen, as shown on Fig. 4-11. Oxidants that are used include chlorine, potassium permanganate (KMnO4), oxygen,
Figure 4-10
Typical process train for removal of dissolved gases and/or volatile constituents from groundwater.
Raw water from ground- water source
Treated water to distribution system
storage
Liquid processing
Residuals processing and management
Pressurized granular media filtration
Disinfectant Clearwell
Water return from waste washwater recovery system, solids dewatering, and filter-to-waste
or disposal
Waste wash- Filter-to-waste
water to water water to recycle
Filter backwash water
Stripping Air tower
Off-gas to
activated
carbon ad- recovery system to head of plant
sorption or other control strategy
Figure 4-11
Typical process train for removal of iron and manganese from groundwater.
Raw water from ground- water source
Treated water
to distribution system
storage
Liquid processing
Residuals processing and management
Pressurized
Disinfectant Clearwell
Water return from waste washwater recovery system, solids dewatering, and filter-to-waste
Waste washwater Filter-to-waste
to water recovery water to recycle
system or disposal to head of plant
Filter washwater
pH
adjustment greensand media
filtration

## Slide 5
212
4 Water Quality Management Strategies
Figure 4-12
Typical residual processing options: (a) least mechanically intensive employing sludge storage and dewatering basins, typically used at small and remote treatment plants where adequate land is available; (b) more mechanically intensive employing sludge thickening, sludge storage and dewatering basins, and ﬁlter waste washwater recovery basins, typically used at intermediate size plants where adequate land is available; and
(c) mechanically intensive
employing sludge thickening, ﬁlter waste washwater recovery basins, and mechanical dewatering, typically used at larger water treatment plants.
(a)
(b)
(c)
Thickening
Washwater recovery basin
recovery
basin
Solids to disposal or reuse
Supernatent
Recycle
Solids
Solids
Polymer
Polymer
Solids from sedimentation process
Solids from sedimentation process
Supernatent and Percolate
Mechanical dewatering (e.g., centrifuge, belt filter press)
Thickening
Filtrate
Solids to disposal or reuse
Supernatent
Recycle
Solids
Coagulant
Polymer
Solids Washwater
Water recovered from residuals processing
returned to water treatment
Sludge storage and dewatering basins
Solids to disposal or reuse
Solids from
Filter waste sedimentation
backwash water process
Water recovered from residuals processing
returned to water treatment
Water recovered from residuals processing returned
to water treatment
Sludge storage and dewatering basins
Filter waste backwash water
Filter waste backwash water

## Slide 6
10-7 High-Rate Sedimentation Processes
691
Treated water
Sludge
Sludge
Water to be treated
Solids
recirculation
Chemical addition
Clarified water to weir overflow
Mixing and flocculation zone
Water to be treated
Buoyant media compacted during
clarification
Clarified water collected using overflow weir
Air manifold not used during clarification
Waste washwater
Buoyant media expanded during cleaning cycle
Influent water used to flush reactor during
cleaning
Waste washwater collected in trough during cleaning cycle
Treated water
Air supplied through manifold during cleaning cycle to scour media
Air Cleaning cycle
Clarification cycle
Sludge
Water to be treated
Sludge
Chemical addition
Central vacuum chamber
Vent valve to release vacuum
Vacuum pump
Water level rises under vacuum and falls when vented to pulse sludge bed with accumulated water
Clarified water withdrawn using launders with submerged
orifices (typical)
Laterals from central distribution manifold with downward pointing
orifices (typical)
Optional lamella
plate settlers
Central distribution manifold
Stilling baffles (typical)
Sludge overflow weir
(a)
(b)
(c)
Figure 10-19
Three common types of proprietary reactor clariﬁers: (a) reactor clariﬁer (IDI Accelator), (b) sludge blanket clariﬁer (Pulsator, when optional lamella plates are added, the unit is known as the Super Pulsator), and (c) IDI absorption clariﬁer. (Courtesy of Inﬁlco Degre´mont, Inc.)

## Slide 7
11-2 Principal Features of Rapid Filtration
733
Anthracite
Sand
Underdrains
Lower gullet (filtered water)
Upper gullet (unfiltered water)
Washwater troughs
(a)
(b)
(c)
Figure 11-1
Typical dual-media rapid ﬁlter. (a) Schematic representation of
dual-media ﬁlter. (b) View
of an operating rapid ﬁlter. Washwater troughs are visible below the water surface. Inﬂuent water enters through the central channel, ﬂows through the wall openings for the washwater troughs, and then down through the ﬁlter media, which is below the water surface. (c) Rapid ﬁlter during the backwash cycle. Washwater ﬂows up through the media, pours over into the troughs, and then runs into the central channel.
particles were discussed in detail in Chap. 9. Properly designed and operated rapid ﬁlters can fail quickly if the coagulant feed breaks down or the raw- water quality changes and the coagulant dose is not adjusted accordingly.
Basic Process Description
A typical conﬁguration for rapid ﬁlters is illustrated on Fig. 11-1. The ﬁlter bed is contained in a deep structure that is typically constructed of reinforced concrete and open to the atmosphere. The rapid ﬁltration cycle consists of two stages: (1) a ﬁltration stage, during which particles accumulate, and (2) a backwash stage, during which the accumulated material is ﬂushed from the system. During the ﬁltration stage, water ﬂows downward through the ﬁlter bed and particles collect within the bed. The ﬁltration stage typically lasts from 1 to 4 days.
During the backwash stage, water ﬂows in the direction opposite to
remove the particles that have collected in the ﬁlter bed. Efﬁcient removal of collected solids is a key component of rapid ﬁltration systems, so while the backwashing stage is very short compared to the ﬁltration stage, it is a very important part of the ﬁltration cycle.

## Slide 8
736
11 Granular Filtration
Filtration
Conventional filtration.
Most common filtration system. Used with any surface water, even those with very high or variable turbidity. Responds well to rapid changes in source water quality.
Coagulant Flocculation
Sedimentation Filtration
Roughing filter
Mixing
Direct filtration.
Good for surface waters without high or variable turbidity. Typical source waters are lakes and reservoirs, but usually not rivers. Raw-water turbidity < 15 NTU.
Coagulant Flocculation
Filtration
Mixing
Two-stage filtration.
Preengineered systems used in small treatment plants (also called package plants). Raw-water turbidity < 100 NTU.
Mixing
In-line filtration (also called contact filtration).
Requires high-quality surface water with very little variation and no clay or sediment particles. Raw-water turbidity < 10 NTU.
Coagulant
Filtration
Coagulant
Mixing
Figure 11-3
Classiﬁcation of rapid ﬁltration by pretreatment level.