## Slide 1
Stage 1 DBPR analytical and monitoring requirements for chlorine and chloramines and associated compliance and reporting requirements.
Under the Stage 2 DPBR, compliance dates are dependent on the population served by a system or the population served by the largest system within a combined distribution system (CDS). A CDS is an interconnected distribution system consisting of the distribution systems of wholesale systems and of the consecutive systems that receive some or all of their finished water from those wholesale systems.
Table 1 - Stage 2 DBPR TTHM and HAA5 Compliance Monitoring Compliance Dates
IF YOU ARE THIS TYPE OF SYSTEM | YOU MUST HAVE BEGUN COMPLYING WITH SUBPART V TTHM/HAA5 MONITORING BY: 1
Systems that are not part of a combined distribution system and systems that serve the largest population in the combined distribution system | 
(1) System serving ≥100,000 | April 1, 2012
(2) System serving 50,000-99,999 | October 1, 2012
(3) System serving 10,000-49,999 | October 1, 2013
(4) System serving <10,000 | October 1, 2013 if no Cryptosporidium monitoring is required under Long-Term 2 Enhanced Surface Water Treatment Rule (LT2ESWTR) OR October 1, 2014 if Cryptosporidium monitoring is required under LT2ESWTR
Other systems that are part of a combined distribution system | 
(5) Consecutive system or wholesale system | at the same time as the system with the earliest compliance date in the combined distribution system
1 The state may grant up to an additional 24 months for compliance with MCLs and operational evaluation levels if the water system is required to make capital improvements to comply with an MCL.
3. Summary of Regulatory Requirements
MRDLGs and MRDLs for disinfectants only; MCLGs and MCLs for disinfection byproducts
EPA established maximum residual disinfectant level goals (MRDLGs) and MRDLs for three chemical disinfectants – chlorine, chloramine and chlorine dioxide – and established MCLGs and MCLs for TTHM, HAA5, chlorite and bromate, as described in the tables below. All MCLs and MRDLs are in milligrams per liter (mg/L).
Table 2 - Regulated Disinfectants
Regulated Disinfectants | MRDL (mg/L) | MRDLG (mg/L)
Chlorine | 4.0 as Cl2 | 4 as Cl2
Chloramines | 4.0 as Cl2 | 4 as Cl2
Chlorine dioxide | 0.8 as ClO2 | 0.8 as ClO2

## Slide 2
Table 3 - Regulated Contaminants
Regulated Contaminants | MCL (mg/L) | MCLG (mg/L)
TTHM | 0.080 | Three individual MCLGs were established: Bromodichloromethane at Zero Dibromochloromethane at 0.06 Bromoform at Zero
HAA5 | 0.060 | Two individual MCLGs were established: Dichloroacetic acid at Zero Trichloroacetic acid at 0.3
Bromate (plants that use ozone) | 0.010 | Zero
Chlorite (plants that use chlorine dioxide) | 1.0 | 0.8
Monitoring plan
Each water system must develop and implement a monitoring plan that details how it will meet all applicable requirements. The monitoring plan must include specific locations and schedules for collecting samples, and how the water system will calculate compliance with MCLs, MRDLs and removal requirements. The monitoring plan must be kept on file for state and public review, and must contain monitoring plans for any other systems in the CDS if the state has allowed combined monitoring.
Laboratory methods and certification
Analysis for DBPs must be conducted by laboratories that have been certified by EPA or the state. Chlorite measured at the entrance to the distribution system is a trigger, not an MCL compliance sample, and may be analyzed by a party approved by the state. For disinfectants and other specified parameters that EPA believes can be adequately measured on-site (for example, for samples that may deteriorate before reaching a certified laboratory), EPA requires that analyses be conducted by a party approved by the state. Additional information on approved methods can be found on EPA’s website at: https://www.epa.gov/dwanalyticalmethods.
Monitoring
EPA has developed compliance monitoring schemes for each MRDL, MCL and treatment technique to be protective of acute and chronic health concerns. The compliance monitoring requirements vary by the size and type of the water system, the treatment employed and the disinfectant used. In many cases, water systems may reduce monitoring frequencies after establishing a baseline. In some cases, water systems that exceed an MCL or MRDL may need to increase the number of samples or monitoring frequency.
Compliance
Compliance is based on a running annual average (RAA) calculated quarterly, locational running annual average (LRAA) calculated quarterly, a single sample result or an average of a selected number of samples, depending on which disinfectant or DBP is being monitored.