## Slide 1
“Demand Charge” ($/kw) is imposed on consumer by the utility company to compensate it for the design & upkeep of equipment to meet the peak power draw by the consumer. The demand charge is in addition to the regular energy
consumption charge ($/kw). The demand charge is based upon highest power consumption over any 15 minute period during the billing cycle. Oversized and inefficient equipment (motors & pumps) would mean higher demand charges.
Given Calculate
What is the required water horsepower to pump 300 GPM if the suction head and discharge heads are constant at 20 ft and 120 ft respectively and the system head losses are 5 ft.
Given and existing & replacement Calculate savings
An older motor which is 82% efficient is to be replaced by a new, 94% efficient motor. Calculate the annual savings for the new motor given the output horsepower from both motors is 180Hp and the elec- tricity cost is $0.075/kWh & the motor operates 24 hours per day throughout the year.
Input Hp
$
Eff:
Output Hp Brake Hp
Eff: p
m
Water Hp
7.95Hp
300 GPM x (120-20+5 ft) =
3960
GPM-ft
Hp
Solution:
Brake Hp
0.5 = 8Hp = Brake Hp = 16Hp
Given Calculate
Find the input Hp Given the water Hp equals 8Hp and the pump and motor efficiencies are 80% and 50% respectively.
Solution:
Step 1: Find knowing & Step 2: Find knowing &
0.8 = Brake Hp = 16 Input Hp Input Hp
20Hp
0.8
Input Hp = 16 =
Annual (218.5-191.5)HpX 0.746 Kw X
Savings Hp
=
Hp input to = 180 = 191.5Hp Hp input to = 180 = 218.5Hp
new motor 0.94 old motor 0.82
$0.075 $23,779
Kwh Year
Flow * Head
365 x 24 hrs
Year
X
Head associated with energy losses due energy losses due to friction
Head associated with the height the water has to be raised
Total Dynamic Head
Total equivalent height of water column needed to pump
Calculating Static Head
Case A:
Initial water level above pump
Suction
Head (x)
Discharge Head
Static Head
Final Water Surface
El = y
Case B:
Initial water level below pump
Friction Head
Static Head
Head
Discharge Head
Static Head
El = x El = 0
El = -x
Suction
lift (x)
Static Head
= y-x
= y-(-x)
= y+x
Static Head